## Final Requirements Table

## This document contains the finalized list of primary functional requirements (1.1) and 		DfX requirements (1.2) for the selected Value Proposition stated below:

“Leverage local, grid-agnostic solar energy to enable water heating to sanitize existing water supply from Vibrio Cholerae in Malawi schools.”

## Primary Functional Requirements

| Objective | Metric(s) | Criteria | Constraint(s) | Justification |
| --- | --- | --- | --- | --- |
| Should heat water completely through solar energy | True/False | --- | Must be true (the heating must be powered by solar energy, but there is flexibility for other electronic components) | Malawi experiences significant solar irradiance. Solar powered water heating projects have been successfully implemented in Malawi, and officials say there is a need for more projects like these. |
| Must keep water at target temperature for a satisfactory time interval | Time (minutes) | Longer is better up to more than 2 minutes | Must keep water at target temperature (70°C) for at least 2 minutes | From the WHO: keeping water at 70°C for 2 minutes is the recommended heating time for inactivating >99% of V. cholerae cells (the bacteria that causes cholera). *Note: We are deciding on >99% reduction and not a less strict requirement (ex. 90%) because much of the WHO water sanitation material we have seen assumes a >99% reduction, even though it is never explicitly said that >99% is required. Also, EPA standards for water purifiers require a 5-6 log reduction in bacteria, which corresponds to >99% reduction. |
| Must heat water up to a satisfactory target temperature | Temperature (Celsius) | Plateau from 70-100°C. Higher is worse after 100°C. | Must get water temperature to 70°C Should not get water temperature above 100°C | From the WHO: 70°C is the recommended target temperature for inactivating >99% of V. cholerae cells. Getting the water to boil isn’t necessary to inactivate V. cholerae. It might also be counterproductive (ex. pressure changes and evaporation might place stress on storage tank). |
| Should store sanitized water | True/False | --- | Must be true | Storing sanitized water is necessary for students and staff to use it later. |

## 1.2	DfX and other Requirements

## Requirements are grouped under High-Level Objectives (HLOs).

| Objective | Metric(s) | Criteria | Constraints | Justification |
| --- | --- | --- | --- | --- |
| HLO 1: Design for Efficiency |  |  |  |  |
| Must use solar power efficiently | Thermal efficiency: ηth = Qout/Qin | Higher is better | Must be at least 45% | https://dspace.mit.edu/handle/1721.1/68524 https://www.sciencedirect.com/science/article/pii/B9780444642417503037 (2.3) |
| Heating tank should be thick enough to be efficiently insulated | R value (a measure of thermal resistance) (K⋅m^2/W) | Higher is better | Depends on the materials and the dimensions (see standards) | 2019 Building Energy Efficiency Standards - Reference Ace v23 |
| Solar collector must be angled toward the Sun efficiently | Solar collector tilt angle in degrees | --- | If fixed, it must be equal to the local latitude. If not fixed, it should follow the direction of maximal sunlight throughout the day. | ISO: 9459-4:2013 states that a fixed collector tilt angle should be equal to the local latitude. |
| HLO 2: Design for Affordability |  |  |  |  |
| Should be low material cost | Cost (CAD) | Lower is better | --- | Lower material costs would make it easier for users to adopt technology. Lower material costs often contribute to lower product costs, and product cost is a significant barrier to product adoption by low-income communities. Material costs are easier for engineering designers to find out (as opposed to costs of manufacturing, distribution, maintenance etc.). |
| Should have low maintenance costs | Cost (CAD) | Lower is better | --- | Lowers barrier to product adoption by low-income communities. |
| HLO 3: Design for Safety |  |  |  |  |
| Water is dispensed at a safe temperature | Temperature (Celsius) | Downward parabola, zeroes at 10 and 49°C | Should be below 49°C Should be higher than 10°C | According to the U.S. Environmental Protection Agency (EPA), hot tap water should be no hotter than 120°F (49°C) to prevent scalding injuries. Minimum recommended water temperature is 10°C. Room temperature or slightly cool water is usually preferable. |
| Any component that comes into contact with water must not transfer harmful chemicals into the water | True/False | --- | Must be true | Since it is important that water remains uncontaminated. Potential contaminants: Types of Drinking Water Contaminants ¦ US EPA |
| Water heating components must be made of materials able to withstand high temperatures | Creep limit | Higher is better | Must not creep up to 100 degrees Celsius | https://www.nationalboard.org/Index.aspx?pageID=181 |
| Must seal water storage containers when not in use | Yes/No | --- | Must be yes | This is a simple but effective strategy to prevent water recontamination. The CDC lists covering water storage containers as one of the steps to prevent cholera. |
| Sensors should not overheat under normal operating conditions | Temperature in Celsius | --- | Refer to relevant datasheets (depends on sensors used) | Overheating can decrease the efficiency of components and eventually lead to safety risks. The Effects of Heat on Electronic Components (researchgate.net) |
| HLO 4: Design for Reliability |  |  |  |  |
| Should be durable | Time until failure (years) | Higher is better | Should last for at least 20 years | A solar thermal system should last at least 20 years without losing its efficiency |
| Must operate for necessary number of days | Number of days of the school year (days) | Higher is better | Must work for the days within individual school terms of a cumulative total of 210 days per year | Malawi primary school students have 2 terms of 15 weeks (2x15x5 = 150 days) and 1 term of 12 weeks (12x5 = 60 days) = 210 total days of school https://www.education.gov.mw/ (2023-2024) |
| HLO 5: Design for Usability |  |  |  |  |
| Must disinfect enough water for daily school use | Water disinfection capacity (L/day) | Higher is better up to 35kL. (Plateaus after 35kL) | Should be at least 21.6kL | Section 7.6 outlines how to measure and report hot water storage volume: https://www.iso.org/standard/66761.html, 18 L per day per child in public primary schools (Water consumptions in public schools - ScienceDirect), 1200 students in a Malawi primary school (but depends on the school) Taking the stats above, we calculate 18*1200 = 21.6kL/day of water consumption A typical primary school in South Africa uses up to 35kL of water per day, but this statistic is presented as a problematic overuse of water (ie. water is wasted). We’re extrapolating this to Malawi primary schools (of similar size) to mean that any water capacity beyond 35kL/day adds no extra value. |
| Any components that are meant to be moved frequently by users should be lightweight | Weight of component (kg) | Lower is better | Should be less than 16 kg | The guidelines suggest that the maximum weight men should lift at work is 25kg for loads held close to the body at around waist height. Maximum weight guidelines recommend lower weights for women, around 16 kg. |
| Should be easy to maintain | # of cleaning instances | Lower is better | --- | Minimizes disruptions to daily operations and enhances efficiency of facility management |