System Automation Testing Protocol

This testing protocol specifically focuses on collecting data from thermistors and liquid level sensors and integrating them with motors to perform an automatic water dispensing system that relies solely on water temperature and height.

Note that two slightly different software programs are running simultaneously on two different computers: one for the boiling to hot water tank, and the other for the hot to cold water tank. Ideally, both systems should open, or close valves based on readings from the liquid level sensor. However, due to the lack of sensors, the liquid level sensor is only attached to the cold-water tank. Therefore, for prototyping purposes, it is assumed that water from the boiling to hot water tank will be dispensed entirely based on its flow rate.

- Specification 1: Detect the Change in the Temperature

The thermistor used for the prototype must detect temperature changes and properly convert the resistance value to more intuitive temperature values in Celsius.

Note that since there is no thermometer, measuring the relative temperature and effectively detecting changes in temperature are being tested.

- Normal Operation

Testing Protocol

- Make sure the circuit is connected correctly based on the “Circuit_Diagram.png” located in 0106C_DesignDossier/(3) Phase3/Automated Valve Subsystem/Software/System Diagrams.

- Connect the computer to Arduino Nano with USB. Open Arduino IDE and open “sensors.ino”. The file can be found in 0106C_DesignDossier/(3)_Phase3/Automated_Valve/Subsystem/Software/Arduino_IDE/Sensors.

- Click “Upload” button on the top left corner of Arduino IDE. Click “Tools” and “Serial Monitor”.

- Leave the thermistor without any thermal contact, observe the result, and compare it against the expected result. Refer to Table 1, A1. The result will be the reference temperature.

- Contact the thermistor with your hands, observe the result, and compare it against the expected result. Refer to Table 1, A2.

- Contact the thermistor with cold iced water, observe the result, and compare it against the expected result. Refer to Table 1, A3.

- Contact the thermistor with hot water, observe the result, and compare it against the expected result. Refer to Table 1, A4.

Table 1: Collected Data from Testing Protocol Specification 1

See videos in ../Automated_Valve_Subsystem/Software/Software_Test_Videos/Specification_1

| Action | Expected Output | Observed Output |
| --- | --- | --- |
| A1. Leave the thermistor without any thermal contact | The temperature is room temperature (around 22~25*C). | The temperature is room temperature (around 23.0~24.0*C). |
| A2. Contact the thermistor with your hands | The temperature is average body temperature (around 30~35*C). | The temperature is average body temperature (around 31.0~32.0*C). |
| A3. Contact the thermistor with cold iced water | The temperature is lower than the room temperature measured in A1. | The temperature is around 14.5*C, which is lower than the measured room temperature 23.5*C. |
| A4. Contact the thermistor with hot water | The temperature is higher than the room temperature measured in A1. | The temperature is around 58.0*C, which is higher than the measured room temperature 23.5*C. |

- Specification 2: Read the Water Level

The liquid level sensor used for the prototype must detect the water level with an error margin of

±0.5 cm.

- Normal Operation

Testing Protocol

- Make sure the circuit is connected correctly based on the “Circuit_Diagram.png” located in 0106C_DesignDossier/(3) Phase3/Automated Valve Subsystem/Software/System Diagrams.

- Connect the computer to Arduino Nano with USB. Open Arduino IDE and open “water_level_sensor.ino”. The file can be found in 0106C_DesignDossier/(3)_Phase3/Automated_Valve/Subsystem/Software/Arduino_IDE/Sensors.

- Since the eTape liquid level sensor is sensitive, calibration is required. Observe the printed resistance values and adjust the parameters of the equation that converts resistance values to water level values in cm.

- Click “Upload” button on the top left corner of Arduino IDE. Click “Tools” and “Serial Monitor”.

- Leave the liquid level sensor without any contact with the water, observe the result, and compare it against the expected result. Refer to Table 2, A1.

- Begin at 2.0 cm, then gradually submerge the liquid level sensor in water by 4.0 cm increments. Observe the results and compare them against the expected outcomes. Refer to Table 2, A2, A3, A4, A5.

Table 2: Collected Data from Testing Protocol Specification 2

See videos in ../Automated_Valve_Subsystem/Software/Software_Test_Videos/Specification_2

| Action | Expected Output | Observed Output |
| --- | --- | --- |
| A1. Leave the liquid level sensor without any contact with the water | The water level is 0.0 to 0.5 cm. | The water level is 0.0 cm. |
| A2. Pour the water up to 2.0 cm | The water level is in the range of 1.5 to 2.5 cm. | The water level is 1.65 cm. |
| A3. Pour the water up to 6.0 cm | The water level is in the range of 5.5 to 6.5 cm. | The water level is in the range of 5.33 to 6.31 cm. |
| A4. Pour the water up to 10.0 cm | The water level is in the range of 9.5 to 10.5 cm. | The water level is in the range of 9.38 to 10.33 cm. |
| A5. Pour the water up to 14.0 cm | The water level is in the range of 13.5 to 14.5 cm. | The water level is in the range of 14.15 to 14.42 cm. |

- Specification 3: Dispense Water from Boiling to Hot Tank Based on the Readings

The following automation system checks if the water in the boiling water tank has reached a temperature of 40 degrees, waits for 10 seconds, opens the valve for 20 seconds (assume it is the flow rate), and then closes the valve.

Note that more detailed description and state diagram can be found in 0106C_DesignDossier/(3) Phase3/Automated Valve Subsystem/Software/System Diagrams.

- Normal Operation

Testing Protocol

- Make sure the circuit is connected correctly based on the “Circuit_Diagram.png” located in 0106C_DesignDossier/(3) Phase3/Automated Valve Subsystem/Software/System Diagrams.

- Connect the computer to Arduino Nano with USB. Open Arduino IDE and open “Boiling_to_Hot.ino”. The file can be found in 0106C_DesignDossier/(3)_Phase3/Automated_Valve/Subsystem/Software/Arduino_IDE/Automation_Final.

- Click “Upload” button on the top left corner of Arduino IDE. Click “Tools” and “Serial Monitor”.

- Submerge the thermistor attached to the boiling water tank in water that has not reached a temperature of 40 degrees. Observe the result and compare it against the expected result. Refer to Table 3, A1.

- Submerge the thermistor attached to the boiling water tank in water that has reached a temperature of 40 degrees. Observe the result and compare it against the expected result. Refer to Table 3, A2.

- After detecting the water temperature, the system will count up to 10. Then, it will open the valve. observe the result and compare it against the expected result. Refer to Table 3, A3.

- After the valve is opened, the system will keep it open for 20 seconds until 100% of the water from the boiling tank is dispensed, then close the valve. Observe the result and compare it against the expected outcome. Refer to Table 3, A4.

Table 3: Collected Data from Testing Protocol Specification 3

See videos in ../Automated_Valve_Subsystem/Software/Software_Test_Videos/Specification_3

| Action | Expected Output | Observed Output |
| --- | --- | --- |
| A1. Submerge the thermistor (boiling) that has not reached 40 degrees. | The system will not start counting. | The system does not start counting; it just keep printing out the temperature value. |
| A2. Submerge the thermistor (boiling) that has reached 40 degrees. | The system will start counting. | The system prints out the message: “The water has reached over 40C. Start counting up to 10.” and start counting. See video titled “Hot Water in the Boiling Tank.mov”. |
| A3. After counting to 10 | The system will open the valve 1 and start dispensing the water | The system prints out the message: “The water has reached over 40*C for 10 seconds. OPEN THE VALUE” and the valve is open. See video titled “Hot Water in the Boiling Tank.mov”. |
| A4. The system’s valve has opened for 20 seconds | The water will be 100% dispensed and the valve 1 will be closed | The system prints out the message: “100% dispensed CLOSE THE VALVE” and the valve is closed. See video titled “Hot Water in the Boiling Tank.mov”. |

- Edge-Case 1: Unexpected Drop in the Water Temperature

This test is intended to simulate an unexpected sudden drop in the water temperature in the boiling water tank while counting to 10.

Testing Protocol

- Make sure the circuit is connected correctly based on the “Circuit_Diagram.png” located in 0106C_DesignDossier/(3) Phase3/Automated Valve Subsystem/Software/System Diagrams.

- Connect the computer to Arduino Nano with USB. Open Arduino IDE and open “Boiling_to_Hot.ino”. The file can be found in 0106C_DesignDossier/(3)_Phase3/Automated_Valve/Subsystem/Software/Arduino_IDE/Automation_Final.

- Click “Upload” button on the top left corner of Arduino IDE. Click “Tools” and “Serial Monitor”.

- Submerge the thermistor attached to the boiling water tank in water that has reached a temperature of 40 degrees. Observe the result and compare it against the expected result. Refer to Table 3, A1.

- After detecting the water temperature, the system will count up to 10. While it is counting, submerge the thermistor attached to the boiling water tank in ice cold water. Observe the result and compare it against the expected result. Refer to Table 3, A2.

Table 4: Collected Data from Testing Protocol Specification 3 Edge-Case 1

See videos in ../Automated_Valve_Subsystem/Software/Software_Test_Videos/Specification_3

| Action | Expected Output | Observed Output |
| --- | --- | --- |
| A1. Submerge the thermistor (boiling) that has reached 40 degrees. | The system will start counting. | The system is in the process of counting. See video titled “Edge Case.mov”. |
| A2. Submerge the thermistor (boiling) in ice-cold water while it is counting. | It will stop counting and go back to the initial state. | The system stops counting at 8 and prints out the temperature in the boiling water tank again. See video titled “Edge Case.mov”. |

- Specification 4: Dispense Water from Hot to Cold Tank Based on the Readings

The following automation system checks if the water in the hot water tank has cooled down to a temperature of 20 degrees, monitors the water level in the cold-water tank, opens the valve while there is available space in the cold-water tank, and then closes the valve once the cold-water tank has reached its capacity.

Note that more detailed description and state diagram can be found in 0106C_DesignDossier/(3) Phase3/Automated Valve Subsystem/Software/System Diagrams.

- Normal Operation

Testing Protocol

- Make sure the circuit is connected correctly based on the “Circuit_Diagram.png” located in 0106C_DesignDossier/(3) Phase3/Automated Valve Subsystem/Software/System Diagrams.

- Connect the computer to Arduino Nano with USB. Open Arduino IDE and open “Hot_to_Cold.ino”. The file can be found in 0106C_DesignDossier/(3)_Phase3/Automated_Valve/Subsystem/Software/Arduino_IDE/Automation_Final.

- Click “Upload” button on the top left corner of Arduino IDE. Click “Tools” and “Serial Monitor”.

- Submerge the thermistor attached to the hot water tank in water that has not reached below a temperature of 20 degrees. Observe the result and compare it against the expected result. Refer to Table 5, A1.

- Submerge the thermistor attached to the hot water tank in water that has reached below a temperature of 20 degrees. Observe the result and compare it against the expected result. Refer to Table 5, A2.

- After the water has reached below the temperature of 20 degrees, but the water level in the cold-water tank is above 10 cm. Observe the result and compare it against the expected result. Refer to Table 5, A3.

- After the water has reached below the temperature of 20 degrees, and the water level in the cold-water tank is below 10 cm. Observe the result and compare it against the expected result. Refer to Table 5, A4.

- After valve 2 is opened, it will continuously update the water level value of the cold-water tank. The water level has reached 10 cm. Observe the result and compare it against the expected outcome. Refer to Table 5, A5.

Table 5: Collected Data from Testing Protocol Specification 4

See videos in ../Automated_Valve_Subsystem/Software/Software_Test_Videos/Specification_4

Note that ideally, the threshold should be 20 degrees. However, since the cold water has warmed up, the threshold has been adjusted.

| Action | Expected Output | Observed Output |
| --- | --- | --- |
| A1. The water temperature in the hot water tank is above 20 degrees. | The system will not open the valve. | The system keeps printing out the temperature and water level values; it does not open the valve. See video titled “A1 Hot Water in the Hot Water Tank.mov”. |
| A2. The water temperature in the hot water tank is below 20 degrees. | The system will check the water level in the cold-water tank. | The system prints out the message: “The water has reached below 22*C. Check 1f there 1s a space for the water.” See video titled “Cold Water in the Hot Water Tank.mov”. |
| A3. A2 is satisfied, but the water level in the cold-water tank is higher than 10 cm. | The system will not open the valve. | The system prints out the message: “The water has reached below 22*C. Check 1f there 1s a space for the water.” See video titled “Cold Water in the Hot Water Tank.mov”. |
| A4. A2 is satisfied, and the water level in the cold-water tank is lower than 10 cm. | The system will open the valve. | The system prints out the message: “There is a space for the water :) OPEN THE VALUE” and the valve and the valve is open. See video titled “Cold Water in the Hot Water Tank.mov”. |
| A5. While water is being dispensed, the water level reaches 10 cm. | The system will stop dispensing and close the valve. | Ideally, it should be tested, but due to the sensitivity of the liquid level sensor, testing was not possible. The system prints out the message: “Water level in the cold water tank: 0.00 cm”. |

- Edge-Case 1: Unexpected Increase in the Water Temperature

This test is intended to simulate an unexpected sudden increase in the water temperature in the hot water tank while dispensing cooled-down water to the cold tank.

Testing Protocol

- Make sure the circuit is connected correctly based on the “Circuit_Diagram.png” located in 0106C_DesignDossier/(3) Phase3/Automated Valve Subsystem/Software/System Diagrams.

- Connect the computer to Arduino Nano with USB. Open Arduino IDE and open “Hot_to_Cold.ino”. The file can be found in 0106C_DesignDossier/(3)_Phase3/Automated_Valve/Subsystem/Software/Arduino_IDE/Automation_Final.

- Click “Upload” button on the top left corner of Arduino IDE. Click “Tools” and “Serial Monitor”.

- Submerge the thermistor attached to the hot water tank in water that has reached a temperature below 20 degrees. For testing a specific edge case, assume there is space in the cold-water tank. Observe the result and compare it against the expected outcome. Refer to Table 6, A1.

- While the system is dispensing, submerge the thermistor attached to the hot water tank in hot water. Observe the result and compare it against the expected outcome. Refer to Table 6, A2.

Table 6: Collected Data from Testing Protocol Specification 4 Edge-Case 1

See videos in ../Automated_Valve_Subsystem/Software/Software_Test_Videos/Specification_4

| Action | Expected Output | Observed Output |
| --- | --- | --- |
| A1. Submerge the thermistor (hot) that has reached below 20 degrees and there is a space in the cold water tank. | The system will open valve 2 and start dispensing. | Valve 2 is opened. See video titled “Edge Case.mov”. |
| A2. Submerge the thermistor (hot) in hot water while it is dispensing. | It will stop dispensing, close valve 2, and go back to the initial state. | The system prints out the message: “Water temperature is higher than 22*C. CLOSE THE VALVE” and the valve is closed. See video titled “Edge Case.mov”. |